## Slide 1: Operations and Maintenance of Wastewater Stabilization Ponds
North Dakota Operator Training
2021
Susan Hazelett, PE

## Slide 2: Presentation Overview
Background
Operations
Algae
Phosphorus Removal
Maintenance
Troubleshooting
Questions

## Slide 3: Background

## Slide 4: Definitions
Biological Oxygen Demand (BOD)
  The amount of oxygen consumed by bacteria while they decompose organic matter
Total Suspended Solids (TSS)
  The suspended particles that are NOT dissolved and can be removed via a filter
pH
  The acidity or basicity/alkalinity of a solution

## Slide 5
Minimum of 180 Days Storage
Stabilization Ponds Basic Design
3’ freeboard
2’ sludge storage
Operating Volume 3 feet

## Slide 6: Microbial Systems
Bacteria
  Decomposes organic matter (reduce BOD)
  Oxidize inorganic compounds (Ammonia, H2S,Nitrate)
  Feed other members of the food chain
Algae
  Supply oxygen to aerobic bacteria
  and other life forms
  Elevate pH during day– pathogen kill,
  precipitate metals, odor control,
  ammonia volatilization
  Can also cause TSS and pH violations
  Consume oxygen at night and lower pH

## Slide 7: Microbial Systems
Protozoa
Control pathogens
Consume organic matter
Lower BOD and TSS
Higher Life Forms (Daphnia, rotifer, leeches, nematodes)
Digests organic matter
Consume algae, protozoa and nematodes
Clarify water

## Slide 8: Symbiotic Cycle
Sunlight
Algae
Nutrients
Bacteria
Carbon Dioxide
Oxygen
Organic Matter

## Slide 9: Yearly Variations
J
F
M
A
M
J
J
A
S
O
N
D
Discharge Windows
Storage
Storage
Algae
BOD
Bacterial
Activity
pH
Month

## Slide 10: NDNPDES Permit Limits
Biochemical Oxygen Demand (BOD5)
  25 mg/L
Total Suspended Solids (TSS)
  30-45 mg/L
Fecal Coliform (E. coli)
  200 colonies/100 mL (usually seasonal)
pH
  6(7)-9 SU
  Total Phosphorus
  None yet

## Slide 11: Operations

## Slide 12: Operational Steps
Use Fill and Draw Type Operation
  Isolate primary cell for raw influent
Make Old Water
  Hold in primary until full, then transfer from primary(s) to final cell
Isolate/Settle in Final Cell

## Slide 13: Operational Steps
Spring
  Operator discharges enough high-quality effluent after solids settle and before algae develops
Fall
  Operator discharges enough high-quality effluent after solids settle and after algae die off
  OR
Summer
  Irrigate or spray site during growing season

## Slide 14: Method of Operation
Series Operation or Parallel Operation

## Slide 15: Series Operation – Two Cell
Primary Cell
Secondary
Cell
Influent
Settle
Transfer
1) All Influent to Primary Cell – Closed Transfer Gates
2) Create Old Water
3) Transfer into Secondary

## Slide 16: Series Operation – Three Cell
1) Influent Into a Primary 4) Create Old Water
2) Create Old Water 5) Transfer to Secondary
3) Transfer to other Primary
Influent
Transfer
Settle

## Slide 17: Parallel Operation – Three Cell
1) Equal Split into both Primary A and Primary B
2) Create Old Water
3) Transfer into Secondary
Influent
Settle
Influent
Transfer
Transfer

## Slide 18: Series vs. Parallel Operation
Series Operation
  Summer
  During discharge
Parallel Operation
  Winter
  High loading

## Slide 19: Moving/Transferring Water

## Slide 20: Guidelines for Transferring
Create Old Water
Six Inches Per Day
Fill Secondary to Max Operating (3’)
Isolate Secondary Before Discharge/Irrigation

## Slide 21: Adequate Elevation Difference
Can you Fill and Isolate the Secondary
HWL of Secondary = LWL of Primary
Transfer Pump Needed?
Pump Size?
  6 inches per day = 100 gpm per acre
Pump Through Control Structure

## Slide 22: Discharging
Discharge Period
Generally:
Acceptable Discharge Periods | 
Spring | March 1 – June 30
Fall | September 1 – December 31
Problem Discharge Periods | 
Summer | July 1 – August 31
Winter | January 1 – February 28

## Slide 23: Discharging
Ice-covered Receiving Water – 100 percent coverage from bank to bank, regardless of ice thickness
Facilities should avoid discharge to ice-covered receiving water regardless of acceptable/problem discharge period

## Slide 24: Discharging How much discharge is enough?
1) Calculate Storage Need
  Days (180) x Average Flow
  = Volume of Storage Needed
2) Calculate Storage Available
  Calculate Volume Available in All Ponds
3) Calculate Total Volume to Discharge
  Storage Need – Storage Available
  = Volume to Discharge
4) Calculate Total Feet to Discharge
  Volume to Discharge/Secondary Pond Size
  = Feet needed to discharge

## Slide 25: Discharge Calculations

## Slide 26: Algae in Ponds

## Slide 27: Algae in Ponds
Algae is an essential component in a healthy pond system
Algae provide needed oxygen to bacteria for waste stabilization
Algae can become problematic, cause high TSS and high pH
Old ponds with high sludge levels, excess nutrients in raw wastewater

## Slide 28: Algae Removal
Natural Die Off
Daphnia
Aquatic Plants
Barley Straw
Chemicals – Call NDDEQ
  Copper Compounds – avoid due to toxicity concerns
  Hydrothol 191,Potassium Permanganate, Sodium Percarbonate

## Slide 29: Daphnia
Pond Filter
Clarifies water, feeds on bacteria and algae

## Slide 30: Aquatic Plants - Coontail
Submersed/Free Floating Plant with NO Roots
Absorbs Nutrients
Releases a Chemical that Inhibits Algae Growth

## Slide 31: Barley Straw
Must be Added Prior to Algae Development
Releases Substance Toxic to Algae

## Slide 32: Copper Compounds
Not recommended due to potential toxicity
Must meet both an effluent limit and receiving water quality limit for copper
Receiving water copper limit depends upon water hardness
Discuss with NDDEQ prior to use

## Slide 33: Hydrothol 191
Approved aquatic algaecide/herbicide
Available as a liquid or granular
Toxic at 0.3 mg/L
Need at least 1.0 mg/L to reduce to less than 45 mg/L
Water temperature greater than 68°F
Pond must be aerobic
Wait at least 4 days before discharge or 7 days before spray

## Slide 34: Potassium Permanganate
Typically used in water treatment for taste and odor
Typical dosage needed
  70 to 165 pounds per acre
Concerns
  Pink/Purple, then straw brown color
  Stain hands
  Safety
    Eye protection
    Reacts with other chemicals; explosive
  Can be toxic to aquatic life

## Slide 35: Phosphorus Removal

## Slide 36: Typical Pond Effluent Phosphorus Concentrations
Low range
  < 2.0 mg/L
Average
  2.0 – 3.0 mg/L
High range
  8 + mg/L
NPDES Permit (if required)
  - 1.0 mg/L

## Slide 37: Typical Chemicals Used
Aluminum Sulfate (Alum)
Ferric Chloride

## Slide 38: Application of Alum
Alum dispersed/mixed into pond contents
  With pontoon or fishing boat
  Piped to mixers in the ponds
Application equipment
  Injection equipment
  Possibly a loading dock
  Storage tanks (boat and land)
Some have applied via a fire hose from dike
Can be labor intensive

## Slide 39: Application of Alum

## Slide 40: Application of Alum

## Slide 41: Chemical Reaction
Chemical reacts with phosphorus
A floc is formed
Settling occurs
Dosage depends on
phosphorus concentration
pH

## Slide 42: Pond Systems Using Alum
To remove 2 mg/L
  Approximately 70 to 150 gallons of liquid alum per million gallons of water in your pond
Cost
  Approximately $2 per liquid gallon delivered but can vary depending on location

## Slide 43: Maintenance

## Slide 44: Maintenance
Extremely important
If neglected, will destroy pond system
Can result in very costly repairs

## Slide 45: Necessary Maintenance
Vegetation
  Submerged
  Floating
Grass
Erosion
Rodents
Floating Mats
Control Structures
Seepage
Road/Fences/Gates/Signs

## Slide 46: Proper Maintenance
Protect the Liner
Reduce Odor/Insect Problems
Prevent Short-Circuiting
Increase Sunlight Penetration
Can Save Costly Repairs in the Future

## Slide 47: The Good

## Slide 48: The Bad …and the Ugly

## Slide 49: Vegetation Concerns
Is it Deep-Rooted?
Is it Affecting Your D.O. Level?

## Slide 50: Cattails
Very Deep, Penetrating Root System

## Slide 51: Removal of Cattails
Pulling Young Plants
Cut and “Drown” Method
  Lower water level and cut near bottom
  Raise water at least three feet above remaining plant
Chemicals
  Approved DEQ aquatic herbicide

## Slide 52: Coontail
Has been Shown to be Very Beneficial
Releases Toxins and Absorbs Nutrients
Not Deep Rooted

## Slide 53: Grass Dikes
Need to be Mowed Frequently for Erosion Control
Recommended at Least Monthly
Good
Bad

## Slide 54: Erosion Control
Durable, Properly Sized and CLEAN Rip Rap is Very Important

## Slide 55: Erosion Control
Old Sidewalks, Bricks, and Cars are NOT Recommended

## Slide 56: Rodent Control
Frequent, Careful Inspection of Dikes is Required
Muskrats, Gophers, Groundhogs
Trapping or ???

## Slide 57: Rodent Control
If Not Addressed, Rodents can Cause Big Problems, including Dike Failure

## Slide 58: Floating Mats
Very Common in the Late Summer
Blue-Green Algae
Filamentous Algae
Duckweed
Sludge ?

## Slide 59: Floating Mats

## Slide 60: Blue-Green Algae

## Slide 61: Filamentous Algae

## Slide 62: Duckweed

## Slide 63: Sludge

## Slide 64: Control Structures
Corrosion
Ventilation
Leakage
  Slide gate
  Valves
  Control structure

## Slide 65: Slide Gates

## Slide 66: Valves and Slide Gates
Valve
Slide Gate

## Slide 67: Seepage
Clay, Synthetic liner
Does system meet seepage
criteria
Desktop water balance
Water balance needed?

## Slide 68: Roads, Signs, Gates, and Fences

## Slide 69: Troubleshooting

## Slide 70: Pond Colors
Dark green – Normal Primary Pond
Light green – Normal Secondary Pond
Dark Pea Soup – Primary Pond – Summer
Black or Grey – Normal after ice-out; overloaded if in summer
Black/Green – Blue green algae
Red streaks/pink – Daphnia under stress

## Slide 71: Pond Issues
Organic Loading
  22 pounds per acre per day primary ponds -design
Adequate Hydraulic Capacity
  Storage for at least 180 days with 3 ft of freeboard
Improper Operations
  Flow through vs. Fill and draw
  Riser pipe on discharge lines

## Slide 72: Outlet Piping

## Slide 73: Odor
Common and unavoidable in spring
If odor lasts longer than 2 weeks, ponds may be overloaded
Split loading between two primary ponds
Sludge accumulation may be an issue
Hydrogen peroxide or Nitrate salts – expensive due to volume to be treated

## Slide 74: Questions? Susan Hazelett Susan.Hazelett@ApexEngGroup.com 701.224.3101